An experimental comparison between commercial hybrid PV-T and simple PV systems intended for BIPV

M. Fuentesa, M. Vivarb, J. de la Casaa, J. Aguileraa

a Grupo IDEA, Universidad de Jaén, Jaén 23071, Spain.

b Department of Electrical Engineering, Universidad de Cádiz, Cádiz 11519, Spain.

Corresponding author: M. Fuentes, Grupo IDEA, Universidad de Jaén, Jaén, 23071, Spain, mfuentes@ujaen.es, phone number: + 34 953212924, fax: +34 953 211967

Abstract: The idea of combining both thermal and photovoltaic collectors in hybrid photovoltaic-thermal (PV-T) modules actually shows a great potential for integration on facades and rooftops of buildings, mainly because of the reduced available space and the benefits of the on-site electricity and thermal generation. The objective of this work is to compare the real performance (experimental data obtained under real sun during a year) of a commercial hybrid PV-T system vs. a simple PV system using microinverters, assessing the suitability of one-unit hybrid PV-T systems vs. two separated units  -PV systems + Thermal systems-  for building integration. The combined efficiency over the span of a full day could reach values up to 80 %, but this apparent high value needs to be analysed in detail. From the experimental results, it can be observed that both systems, PV and PV-T, have a good electrical performance. But the PV-T system output does not benefit from the lower module temperatures that it should achieve from the active cooling in its back, presenting the same performance as the simple PV system. Regarding the microinverters configuration performance, it has been very positive working with high efficiencies above 96 %, justifying its use in this type of applications. In conclusion, the commercial PV-T system has not performed as expected, showing problems with the integration of the active cooling in the back of the PV modules. At this moment, and despite the potential of PV-T systems for BIPV due to space limitations, commercial PV-T systems are still far from PV and Thermal systems using separately.

Keywords: PV-T; commercial; microinverter; hybrid; performance; BIPV.

| Nomenclature |  |  |  |
| --- | --- | --- | --- |
| Tamb | Ambient temperature (ºC) | Pe | Electrical power (W) |
| TenvHtop | Top envelope hybrid temperature (ºC) | VMOD,M | Maximum Voltage (V) |
| TenvPVtop | Top envelope PV system temperature (ºC) | IMOD,M | Maximum Current (A) |
| Tm1 | Back PV module 1 temperature (ºC) | VMOD,OC | Open Circuit Voltage (V) |
| Tinlet | Inlet module PVT temperature (ºC) | IMOD,SC | Short Circuit Current (A) |
| Tinlet_tank | Inlet tank temperature (ºC) | VDC,PV1 | DC voltage PV module 1(V) |
| TenvHbott | Bottom envelope hybrid temperature (ºC) | VDC,H1 | DC voltage Hybrid module 1(V) |
| TenvPVbott | Bottom envelope PV system temperature (ºC) | IDC,PV1 | DC current PV module 1(A) |
| Tm2 | Back PV module 2 temperature (ºC) | IDC,H1 | DC current Hybrid module 1(A) |
| Toutlet | Outlet module PVT temperature(ºC) | IAC,PV1 | AC current PV module 1(A) |
| Ttank | Tank temperature (ºC) | IAC,H1 | AC current Hybrid module 1(A) |
| Tin | Inlet temperature (K) | VDC,PV2 | DC voltage PV module 2 (V) |
| Tout | Outlet temperature (K) | VDC,H2 | DC voltage Hybrid module 2 (V) |
| T0 | Reference temperature, (K) | IDC,PV2 | DC current PV module 2 (A) |
| Q | Flow rate – Hybrid system (l/s) | IDC,H2 | DC current Hybrid module 2 (A) |
| Qt | Useful thermal power (W) | IAC,PV2 | AC current PV module 2 (A) |
| m | water mass flow rate per unit area (kg/s/m2) | IAC,H2 | AC current Hybrid module 2 (A) |
| cp | specific heat of water (J/kg·K) | VAC | AC voltage total (PV+PV-T) (V) |
| EQ | Thermal exergy rate (W) | APV | photovoltaic area, (m2) |
| η0 | Thermal Efficiency | AC | collector area, (m2) |
| Gi | Solar irradiance | ηe | Electrical efficiency |
| WS | Wind speed (m/s) | η | Module efficiency |

1. Introduction

Hybrid photovoltaic-thermal (PV-T) modules aim to convert the solar energy into electrical and thermal energy, increasing the total system efficiency. A PV-T collector typically consists of a PV module with a heat extraction device attached on the back. The purpose of this heat extraction device is twofold: to cool the photovoltaic (PV) module and thus improve its electrical performance; and to collect the thermal energy produced, which would have otherwise been lost as heat to the environment. This collected heat could be used for low temperature applications. There is a crucial problem for the optimal exploitation of PV-T technology. The electricity production from PV cells is favoured by low temperatures, whereas the usability of the thermal energy gets higher at high temperatures. The first systematic research into the possibilities of combining photovoltaic and solar thermal techniques was performed in the early 1980s by a group at MIT. A major research and development work on the PV-T hybrid technology has been done since last 30 years. The scientific literature shows a wide number of studies with research and development in solar PV-T technology: general design and technology [1,2,3], flat plate solar PV-T [4], performance and applications [5] and performance and simulation 6].

As it is a new technology in the early stages of commercialisation, there is a lack of specific standards and certifications, mainly due to the gap on real performance of these PV-T collectors. Policies from governments, with reduced incentives for manufacturers, and low acceptance from final users, are hampering their widespread and full commercialisation now. There are technical studies that could serve as an initial basis for the full development of standards and certification to guarantee performance and to increase the final user acceptance [7]. The standards used to test these systems have been EN 12975-1,2 [8] and ISO 9806 [9] for solar thermal collectors and IEC 60904-1,2 [10,11] for photovoltaic modules. Nevertheless, standard EN 12975-1 has been revised to restructure it and include an extension of the applicability of the standard to cover PV-T collectors [12] and it will been publish soon.

The objective of this experimental work is the comparison the real performance of a fully commercial hybrid PV-T versus a purely PV system, considering that no studies about this case working integrated in a building have been found.

PV-T collectors can be flat plate or concentrating and are classified according to the type of the working fluid use. Figure 1 shows different concepts of this type of hybrid modules. Flat plate thermal solar collectors are the most widely used in the world because of its low cost and easy and cheap maintenance [13] and they are an alternative promising system for low energy applications in residential, industrial and commercial building. Main studies highlight important factors in flat solar thermal collectors in last years [13] such as the effects of the heat sinking [14], the need of good thermal conductivity between the solar photovoltaic cells and the support structure [15,16], and the encapsulation method used (EVA degrades at high temperatures and in some cases it might not be suitable) [15]. The PV-T concept could be very effective, especially when using water as heat removal fluid [17]. Water flat plate PV-T collectors achieve higher overall efficiencies than air systems, due to the higher heat carrying capacity of water [18], and could be divided in two main categories:

- Covered PV-T collectors, characterized by the presence of an air gap between the transparent frontal cover and the absorber, in which a large amount of thermal energy can be produced, with a concurrent rise of the cell temperature, which can compromise the electrical performance.

- Uncovered PV-T collectors, where no air gap is present above the absorber; such collectors produce water at a lower temperature and reduce the overheating for the photovoltaic cells, obtaining higher electrical efficiency, despite the fact that less thermal energy is usually exploited compared to covered components.

Regardless of the lower overall efficiency, the most common product on the market is the latter [19, 20]. For PV-T liquid systems, several manufacturers have tried to develop a PV thermal module, but this has not led to large-scale commercial manufacturing. Several reasons can be brought up to explain this. First, very little has been published on PV-T system and production technology, indicating that this area has scarcely been investigated. Secondly, there is very little experience with PV-T products. Good market research is necessary, especially as PV-T combines aspects of both PV and of solar thermal and these two market fields are quite different. A third reason could be that many of the companies that were involved in the PV-T initiatives were taken over by companies that did not place PV-T in their product range [1]. The main bottlenecks for the commercialization of PV-T products are the lack of economic viability, public awareness, product standardization, warranties and performance certification, installation training and experiences. It is important for the reliability of the technology to be thoroughly assessed with more practical research for widespread its commercial acceptance [3, 4]. In fact, it is possible to find recently reviews about the state of development of PV-T technology around the world, for example at the Indian subcontinent [21].

Despite of its low commercial acceptance, the idea of combining both thermal and photovoltaic collectors actually shows a great potential for integration on facades and rooftops of buildings [22], mainly because of the reduced available space and the benefits of the on-site electricity and thermal generation that can be used for hot water and heating [23]. Several works point out that flat plate PV-T air and water collectors [17] have a great potential on building integration (BIPV-T) [5], both in the envelope and the rooftop, especially when using water as heat removal fluid [24, 25]. A considerable amount of research has been conducted regarding the flat plate water PV-T collector performance [6, 20] due to its higher heat capacity [26]. It has been also demonstrated that these systems can be manufactured with less expensive materials without significant efficiency losses [25]. Another factor contributing to cost reduction is the possibility of using the PV-T systems ‘in’ the buildings rather than ‘over’ them. An example of the latter is the integration of PV-T modules without a back insulation layer, directly in the buildings that provide an enclosed air gap that acts as an insulating barrier.

1.1 Flat-plate PV-T collectors

First scientific works on PV-T collectors mostly relate only to studies that compare hybrid PV-T non-commercial systems (prototypes) with conventional thermal systems. In 2006, Kalogirou and Tripanagnostopoulus [27] constructed and tested a hybrid PV-T solar system for domestic hot water applications. After modelling with TRNSYS, the non-hybrid PV system showed an electrical energy production about 38 % higher than the hybrid system, but it is true that the designed systems covered a large percentage of the hot water needs of the buildings considered. In 2008, Dubey and Tiwari [28] showed a prototype that achieved good results as it was completely autonomous, producing hot water and generating sufficient electricity to power a pump from the thermal system and saving extra electricity for other purposes. There was a significant increase in the instantaneous overall efficiency from 33 % to 64 % from the case totally/partially covered by PV. Bhattarai et al. in 2012 [29] described a hybrid system that presented 58.7 % thermal efficiency vs. 71.5 % thermal efficiency of the purely thermal collector, with an electrical efficiency of 13.7 %. In fact, despite the losses on thermal efficiency due to the hybridisation, the overall efficiency of the PV-T system including the electrical conversion was higher.

Other studies showed not only modelling results but also real experimental results on PV-T solar systems. In 2007, Kalogirou and Tripanagnostopoulus [30] constructed two types of PV-T systems that were tested outdoors for the determination of the steady state thermal and electrical efficiency, one with pc-Si and one with a-Si (polycrystalline and amorphous silicon commercial panels) in combination with water heat extraction units made from copper sheet and pipes. The results showed that the electrical production of the pc-Si solar cells was better than the a-Si ones as expected, but the solar thermal fraction is slightly lower than the amorphous solar cells.

In 2011 Dupeyrat et al. [15] presented the design of a single glazed flat plate PV-T solar collector. They mainly focussed on the heat transfer between PV cells and fluid, and also on the optical properties of materials. The results indicated that the proposed direct lamination of monocrystalline silicon photovoltaic cells on an optimized metal heat exchanger leads to the best results among the investigated concepts with a thermal efficiency of 79 % under PV operation with a corresponding electrical efficiency of 8.8 %.

Thipjak et al. [31] presented the first results on commercial photovoltaic modules (which were amorphous and multi-crystalline silicon) used as solar absorbers in PV-T collectors in 2012. Testing was done with outdoor experiments under the climate of Bangkok. The cell efficiency was 4.0 % and 4.6 %; and the thermal efficiency was 51 % and 49 % for a-Si and mc-Si PV-T, respectively.

Under purely laboratory conditions, Redpath et al. in 2012 [32] presented a comparison of two PV-T. The first was a simple flat collector PV-T design and the second a fixed linear axis CPC-PV-T energy conversion system. After testing under steady state conditions using a solar simulator, they achieved a combined efficiency of 66.8 % and 53.4 % respectively, although the mean electrical conversion efficiency was 0.4 % higher for the CPC-PV-T system.

In 2013, Axaopoulos and Fylladitakis [33] studied a PVT collector based on commercial modules with and absorber constructed of copper tubes, ultrasonic welded on a copper sheet in contact with the rear panel of the photovoltaic module. The experimental model was constructed and tested by an approved centre for solar collector testing for determining its thermal and electrical performance. The annual performance of the PV-T systems showed a 17.7 % solar thermal system efficiency and 9.6 % of PV conversion efficiency as the best figures.

Kim et al. studied in 2014 [34] the energy performance of a building heating system combined with a water-type PV-T collector integrated into the roof. The experimental results showed that the BIPV-T collectors performed at a maximum of 18.9 % of electrical efficiency with an average thermal efficiency of 30 %, while the temperature of the thermal storage tank rose to 40 ºC from 18 ºC.

An innovative glazed PV-T component with water as heat transfer fluid and the construction of a detailed mathematical model for the estimation of its electrical and thermal production was designed by Aste, Leonforte and del Pero in 2015 [35]. Results showed that the PV-T collector was able to convert solar energy in primary energy with an overall efficiency of 42 % which is given by a 13.2 % of electricity (primary energy) and 28.8 % of thermal energy.

Another improved PV-T solar collector designed combined with hexagonal honeycomb heat exchanger was studied by Hussain et al. in 2015 [16]. The thermal efficiency of the system without honeycomb was 27 % and with it was 87 %. The electrical efficiency of the PV module was improved by 0.1 % throughout the range of the mass flow rate.

In another recent study by de Keizer et al. in 2016 [36], results from the electrical and thermal performance of several uncovered PV-T collector prototypes from three different companies were described. Temperatures in the output of the PV-T collectors reached figures from 36 ºC to 50 ºC in summer. The PV efficiency ranged between 12.2 %, 12.9 % and 14.2 % and the thermal efficiency ranged between 25%, 53 % and 36 %, respectively.

Finally, the PV-T hybrid systems developed by Aste et al. in 2016 [19] presented a total efficiency of 68.4 %: 13.8 % corresponding to the photovoltaic electrical efficiency and 54.6 % corresponding to the thermal efficiency.

From the analysed studies it could be deduced that the overall efficiency of a PV-T system increase as it includes both the thermal and electrical production. In general, the electrical efficiency decrease slightly in comparison with the purely PV system efficiency, and the temperature of the water that works as cooling liquid is below the standards for hot water domestic systems. There are multiple designs of PV-T, although m-Si and pc-Si PV commercial modules are the ones who have shown better efficiencies. The main differences among PV-T works that have been found are the heat extraction units.

1.2 Commercial PV-T Systems	There are a few companies that offer PV-T modules among their products. Some of them derive from photovoltaic or thermal ones and other are new. Most of them use the concept of flat type collector prioritising thermal or electrical behaviour. Regarding prices to compare with other technologies, it is very difficult to get a general idea or a representative figure that englobes all PV-T technologies because they depend of the amount of modules, and most of the manufacturers fix a minimum order to sell them. Nevertheless, PV-T systems are usually more expensive than solar-thermal systems, but the range is very wide. PV-T will be competitive  when its penetration in the market is higher and it passes from the early stages of development towards economies of scale. Nowadays it is possible to find a trend of the well-known solar technologies: thermal and photovoltaics. Solar-thermal systems require a relatively high initial investment for a system installation, typically in the range 1.000 – 2.300 € per m2 [37], compared to the 290 -860 € per m2 [38] for small-scaled PV system. Unfortunately, currently it is not possible to give a range per m2 for PV-T, but the IEA Energy Technology perspectives 2012 shows that solar heating has the potential to cover more than 16% of the low-temperature heat use in an energy mix scenario. In Europe, this share translates into a 45% growth of the installed solar-thermal capacity by 2020. Therefore, there is a potential market for PV-T technologies.

To date, no studies about the real performance of fully commercial PV-T product working integrated in a building have been found. The only study related to BIPV-T system is the simulations conducted by Good et al. in 2015 under Nothern European climate [39], where they compared three solar systems: PV, PV-T and thermal in the roof of a building. Results showed that the best performance corresponded to the purely PV systems, but again their data correspond to simulations, not experimental work.

The objective of this experimental work is to compare the real performance of a fully commercial hybrid PV-T system for building integration vs. a purely PV system using microinverters, obtaining real data from experimental work and assessing the suitability of one-unit hybrid PV-T systems vs. two separated units  -PV systems + Thermal systems-  for building integration.

Results will provide valuable information to work on the full development and optimisation of these systems so they can exploit their full potential vs. the independent use of purely photovoltaic and thermal systems.

2. Hybrid PV-T vs. purely PV systems experimental set-up and monitoring system

2.1 Experimental set-up

The two energy systems were installed, one comprising only-PV modules and other including hybrid PV-T modules, specifically a water-type PV-T collector as it was advanced in previous section. A special care has been taken in choosing the PV part from the same technology and manufacturer for both systems, whose electrical characteristics (PV modules) and thermal characteristic (PV-T panels) are shown in the table I. So, the PV structure includes two PV modules, and the PV-T structure includes two PV-T modules as it is depicted in figure 2. Both systems are located in the Solar Jiennense S.L. facilities in Jaén (Spain) facing south with the same tilt, specifically 20º. The reason of this distribution is to compare the performance of a PV system with a PV-T system with the maximum number of similarities if possible, integrated into the roof.

Therefore, four microinverters have been used to check the advantages opposite the central inverters since they allow different azimuth and tilt in small PV systems, reduce the costs for DC cables and, in theory, mismatch and shaded losses will be reduced [35, 40, 41]. Finally, the model StecaGrid300 from Steca has been chosen to connect with each PV module. In this way, the microinverter is working under its optimal efficiency range because its power is 300 Wp and every PV module has 333 Wp in STC (Standard Test Conditions). Each energy system has two PV modules and two microinverters. A scheme is depicted in figure 3.

Table I. Electrical and thermal characteristics of the PV and PV-T panels

| Electrical Data in STC (PV and PVT panels) |  |
| --- | --- |
| Total area | 1.65 m2 |
| Nominal Power | 333 W |
| Maximum Voltage (VMOD,M) | 54.7 V |
| Maximum Current (IMOD,M) | 6.09 A |
| Open Circuit Voltage (VMOD,OC) | 65.3 V |
| Short Circuit Current (IMOD,SC) | 6.46 A |
| Module efficiency (η) | 20.4 % |
| Thermal Data (PVT panels) |  |
| Absorber area | 1.58 m2 |
| Liquid capacity | 3.88 l |
| Flow rate | 30-150 l/h |
| Operating temperature | -20 ºC / 75 ºC |
| Efficiency (η0) | 63 % |
| System pressure | 1.5 bar |
| Test pressure | 2.5 bar |

The use of heat in buildings can roughly be divided into two main areas. First, to keep the interior temperature at a comfortable level in cold seasons and second, the subject in question, for hot tap water which temperature needs around 60 ºC. The thermal system in this work have been installed for heating tap water, and, in this way, the design has followed the same criteria of a commercial solar water heater. Regarding the solar water heating system included in the PV-T structure, both modules are interconnecting in parallel. The configuration of the primary circuit has a tank collector (Solahurt® 180), a pump (Salmson®) with its controller, pipes and valves. The controller is a differential thermometer that compares the temperature of the tank and the output temperature of the PV-T system. The result of this comparison makes work the pump or stop it. The comparison value is fixed by default as it can be show in equations 1 and 2. In this way the fluid of the primary circuit always transfers heat to water.

Toutlet≥Ttank+7 °C→Pump works	(1)

Toutlet<Ttank+2 °C→Pump stops	(2)

Looking for analogies in building integration, both structures have been enclosed with a surrounding wall (see figure 4) to extrapolate the results to systems integrated in buildings. Airflow around building integrated photovoltaics has a significant impact on their hygrothermal behavior and degradation. The potential of reducing the temperature of BIPV using an underneath cavity is experimentally and numerically investigated in literature [42]. A typical problem of BIPV systems is the power loss due to temperature increase, because modules often operate close to the building envelope with low ventilation. It has been found that the mean and the maximum PV temperature associated with hot spots decrease with the increase in pitch angle [22] and air gap [43] related to the way the module is mounted [44,45] . It is well-known that both the electrical efficiency and the power output of a photovoltaic module depend linearly on the operating temperature and it is written on literature, for example [46,47,48] and the relationship wind-temperature [49]. That has been the reason to take care of the design and the later measuring temperature process.

2.2 Monitoring system

A number of parameters have been identified to affect PV-T performance, based on IEC61724 [50] and ISO9459:2 [51] standards. These include mass flow rate, inlet temperature of working fluid, number of covers, absorber to fluid thermal conductance and, in the case of water type PV-T collectors, an absorber plate design parameters such as tube spacing, tube diameter and fin thickness [6, 36]. In our case, three groups of parameters were recorded: meteorological, photovoltaic and thermal data. An AgilentTM 34972A datalogger (22 bit-resolution) was used to monitor all the parameters every 30 s.

2.2.1 Meteorological data

A dedicated meteorological station (Fig. 5) was installed at Solar Jiennense facilities to measure ambient temperature, global irradiance in the systems plane and wind speed. A Pt-100 (CorregeTM Surface 2000) was used for temperature measurement, installed within a radiation shield (YoungTM 14003). Wind speed was measured by an anemometer (Thies ClimaTM 4.3515.51.961) and a calibrated solar cell (NousolTM) installed in the same plane of the photovoltaic system monitored the global irradiance.

2.2.2 Photovoltaic data

Figures 6 and 7 show the electrical schemes used for monitoring the main performance data, for both the purely PV system and the hybrid PV-T. Electrical parameters (current, voltage) are measured before (DC) and after (AC) each microinverter, plus the power of each complete system trying to complement the monitoring system designed in [22, 35]. Back PV module temperatures are also measured, but in the case of the PV-T modules, inlet and outlet fluid temperatures are measured instead. As both systems are installed over a simulated envelope, temperatures from these structures are also monitored. Two sensors are used per envelope: one for the bottom part, and one near the photovoltaic generator.

All temperature sensors are Pt-100 (CorregeTM Surface 2000), DC and AC voltages are monitored directly by the AgilentTM 34972A datalogger, DC currents are measured using a shunt resistor (KainosTM class 0.5, 10 A-60 mV), AC currents are measured with a Hall effect sensor (LEMTM - AT5-B5), and the AC generated powers are monitored by a watimeter (ABBTM - B12 212).These measurements allow us to get the electrical behaviour and different efficiencies. Figure 8 shows most of the sensors used to monitor the electrical data together the four microinverters.

2.2.3 Thermal data

Thermal system data (Fig. 9) included the inlet and outlet temperatures, the tank inlet and outlet temperatures, all measured with waterproof Pt-100 (RSTM Platinum Resistance Probe), and the flow rate of the circulating fluid, measured with a flow metre (RESOLTM V-40). The monitoring system is based on previous studies and experiences [52, 53].

Overall, total number of parameters to be monitored are: 11 temperatures, 4 DC currents, 4 AC currents, 4 DC voltages, 2 AC voltages, 2 system powers, flow rate, global irradiance on the system plane and wind speed. Table II shows the detail of all the recorded parameters.

Table II. Main parameters recorded during the experimental campaign of the PV-T system for BIPV, including meteorological, photovoltaic and thermal data.

| Variable | Symbol | Variable | Symbol |
| --- | --- | --- | --- |
| Ambient temperature | Tamb | Irradiance | G |
| Top envelope hybrid temperature | TenvHtop | Bottom envelope hybrid temperature | TenvHbott |
| Top envelope PV system temperature | TenvPVtop | Bottom envelope PV system temperature | TenvPVbott |
| Back PV module 1 temperature | Tm1 | Back PV module 2 temperature | Tm2 |
| Inlet module PVT temperature | Tinlet | Outlet module PVT temperature | Toutlet |
| Inlet tank temperature | Tinlet_tank | Tank temperature | Ttank |
| DC voltage PV module 1 | VDC,PV1 | DC voltage PV module 2 | VDC,PV2 |
| DC voltage Hybrid module 1 | VDC,H1 | DC voltage Hybrid module 2 | VDC,H2 |
| DC current PV module 1 | IDC,PV1 | DC current PV module 2 | IDC,PV2 |
| DC current Hybrid module 1 | IDC,H1 | DC current Hybrid module 2 | IDC,H2 |
| AC current PV module 1 | IAC,PV1 | AC current PV module 2 | IAC,PV2 |
| AC current Hybrid module 1 | IAC,H1 | AC current Hybrid module 2 | IAC,H2 |
| AC voltage total (PV + PV-T) | VAC | Flow rate – Hybrid system | Q |
| Wind speed | WS |  |  |

2.2.4 Equations for the thermal and electrical efficiency and exergy analysis

In order to evaluate the electric and the thermal power produced by the solar PV-T collector, equations 3 and 4 are the most used. The electrical efficiency, ηe, is the ratio between the electrical power, Pe, and the solar irradiation received per area (eq. 5). The thermal efficiency, ηt, is the ratio between the thermal power and the solar irradiance received (eq. 6).

Pe=ηe·Gi·APV				(3)

Qt=m·cp·AC·Tout-Tin		(4)

ηe=PeGi·APV				(5)

ηt=QtGi·AC=m·cp·Tout-TinGi		(6)

Where:

Pe, electrical power, W.

ηe, electrical efficiency.

Gi, solar irradiance, W/m2.

APV, photovoltaic area, m2.

Qt, useful thermal power, W.

m, water mass flow rate per unit area, kg/s/m2.

cP, specific heat of water, J/kg·K.

AC, collector area, m2.

Tout, outlet temperature, K.

Tin, inlet temperature, K.

ηt, thermal efficiency.

Since electrical and thermal energy are different in nature, it is necessary to take into account the nature of the energy in evaluating or comparing them. For this, concepts based on the exergy theory are adopted. A PV-T collector could produce higher output density than a unit PV module or liquid heating flat-plate solar collector. Thermal energy gain is much larger than electrical energy gain, but it contains much unavailable energy [54].

Exergy is a well-known concept in the context of energy engineering systems, as it measures the equivalent mechanical work of any process or energy source or carrier. The conceptual basis of exergy (or available energy) goes back to both the First and the Second Law of Thermodynamics, therefore exergy analysis allows a wider view than that provided by a simple energy analysis. Now, while electric energy is pure exergy, thermal energy has an exergy content that depends on the temperature at which heat is made available. This issue is particularly relevant in PV-T systems, where the energy yield is highly influenced by the temperature level of the system. However, a certain discrepancy emerges when dealing with the evaluation of the exergy content of a mass flow in relation to its temperature level. Equations 7 and 8 report the two formulations more frequently adopted in the literature.

EQ=m·cp·Tout-Tin·1-T0Tout		(7)

EQ=m·cp·Tout-Tin-T0·lnToutTin		(8)

Where:

EQ, thermal exergy rate. W.

T0, reference temperature, K.

Equation 7 contemplates that the useful product of the PV-T collector is the thermal power extracted by the fluid from the absorber plate, and that this thermal power is made available at the outlet temperature. To this aim, the Carnot Factor (1-T0/Tout) is introduced, where T0 is the reference temperature at which the exergy content of the thermal power is zero. It is adopted by numerous authors. On the other hand equation 8 is based on the Gouy-Stodola Theorem [55] and measures the increase in the exergy content of the fluid related to its temperature lift from Tin to Tout. This approach is followed in a relatively lower number of publications [56]. Another key point is the reference temperature T0. It is generally assumed equal to the actual variable outdoor temperature. However, this would introduce thermodynamic contradictions because a constant T0 should be assumed. In this paper T0 corresponds to the minimum outdoor temperature registered during any given month, as suggested [57], and the first equation will be used, the most accepted in the literature.

3. Experimental results

The two systems were tested and monitored exhaustively during 2014 and 2015 at Solar Jiennense S.L. facilities over the span of full days under different climatic conditions. Jaén is located at the south of Spain, with numerous days of clear sky conditions but with irradiance and ambient temperature values oscillating during the year according to a temperate climate.

Table III presents a summary of the main electrical and thermal performance parameters of four days of experimentation corresponding to different maximum ambient temperatures, from 10 to 38 ºC (winter, spring, summer). Electrical efficiencies are 16 % in summer up to 19 % in winter, mainly due to the higher temperatures at which the PV modules are working, from 68 ºC in summer to 26 ºC in winter.

3.1 Discussion of results

In general, PV-T system electrical efficiencies are slightly lower than the PV system electrical efficiency, which is the opposite case as it would have been expected. Due to the active cooling on the back surface of the PV modules, they should have been working at lower temperatures, and therefore achieved higher electrical efficiencies. Outlet fluid temperatures in the PV-T system were always lower than the back module temperature of the purely PV system, so the back module of the PV-T system should have been at lower temperatures.

Regarding thermal efficiencies of the PV-T system, they ranged from 50 % to nearly 70 % depending on the season, although final tank fluid temperatures were low for a hot water domestic thermal system (maximum of 45.7 ºC in summer but with values down to 18.2 ºC in winter). Combined efficiencies of the PV-T system calculated as the electrical efficiency plus the thermal efficiency could be up to 80 % but it is necessary to analyse the independent parameters solely to understand the real performance and the limitations of the PV-T system. That is the case of exergy, as defined in section 2 with a reference temperature T0 of 273.06 K (0.06 ºC) got in the experiment period, with better figures in hot seasons, but symbolic facing electrical energy, as several authors show in their works [56, 58].

Finally, the use of dedicated microinverters, one per PV/PV-T module, showed an appropriate DC to AC electricity conversion, with efficiencies reaching 96 % on average along the entire testing period.

If we analyse in detail two clear weather days of testing, one corresponding to maximum ambient temperature of 32.8 ºC and global irradiation of 7,686 Wh/m2 (28/03/2015) and another with 10.4 ºC of maximum ambient temperature and 5,595 Wh/m2 of global irradiation (01/02/2015), we can compare the performance of both systems under different conditions.

Fig. 10a shows the global irradiance over the span of the day when maximum ambient temperature is > 30 ºC, along with the DC power generated by the PV and PV-T systems, and  the corresponding back PV module temperature and average fluid temperature in the PV-T system. According to the PV-T fluid temperature, lower than the PV back module temperature, the electrical output of the PV-T system should have been higher than the purely PV system.

Table III. Main parameters corresponding to the electrical and thermal performance of the PV and PV-T systems when operated over the span of a full day under clear, sunny days with different irradiance and ambient temperature conditions according to the temperate climate of Jaén (Spain).

|  | Parameter | PV | PV-T | PV | PV-T | PV | PV-T | PV | PV-T |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Meteorological |  |  |  |  |  |  |  |  |  |
|  | Date (dd/mm/aaaa) | 17/08/2014 |  | 28/03/2015 |  | 16/03/2015 |  | 01/02/2015 |  |  |
|  | Global irradiation (Wh/m2) | 7458 |  | 7686 |  | 7111 |  | 5595 |  |  |
|  | Maximum ambient temperature (ºC) | 38.6 |  | 32.4 |  | 20.7 |  | 10.4 |  |  |
|  | Electrical output |  |  |  |  |  |  |  |  |  |
|  | Maximum back PV module temperature (ºC) | 67.9 | -- | 56.6 | -- | 52 | -- | 25.8 | -- |  |
|  | Maximum outlet fluid temperature (ºC) | -- | 58.2 | -- | 49.5 | -- | 42.2 | -- | 24.7 |  |
|  | Minimum inlet fluid temperature (ºC) | -- | 22.4 | -- | 3.2 | -- | 2.9 | -- | 1.7 |  |
|  | Electrical energy - DC (Wh) | 3958 | 3771 | 4049 | 3910 | 3957 | 3818 | 3473 | 3317 |  |
|  | Electrical energy - AC (Wh) | 3790 | 3596 | 3893 | 3765 | 3785 | 3636 | 3335 | 3142 |  |
|  | Microinverter efficiency (%) | 95.8 | 95.4 | 96.2 | 96.3 | 95.7 | 95.3 | 96 | 94.8 |  |
|  | Electrical efficiency (%) | 16.1 | 15.3 | 16.2 | 15.6 | 17.1 | 16.5 | 19.1 | 18.2 |  |
|  | Thermal output |  |  |  |  |  |  |  |  |  |
|  | Flow rate (kg/s) | -- | 0.1 | -- | 0.1 | -- | 0.1 | -- | 0.1 |  |
|  | Maximum tank temperature (ºC) | -- | 45.7 | -- | 36 | -- | 27.8 | -- | 18.2 |  |
|  | Thermal output energy (Wth·h) | -- | 5253 | -- | 5307 | -- | 3554 | -- | 3488 |  |
|  | Exergy (Wh) | -- | 724 | -- | 637 | -- | 375 | -- | 153 |  |
|  | Thermal efficiency (%) | -- | 70.4 | -- | 69 | -- | 50 | -- | 62.3 |  |
|  | Total / Combined efficiency (%) | 16.1 | 85.7 | 16.2 | 84.6 | 17.1 | 66.5 | 19.1 | 80.5 |  |
|  | Total energy efficiency (electrical+exergy)(%) | 16.1 | 18.5 | 16.2 | 18.1 | 17.1 | 18.1 | 19,1 | 19 |  |

But the graph shows that both PV and PV-T systems generate almost the same electricity, with no major differences. In fact, the PV-T DC power is even slightly lower than the energy produced by the PV system. This difference is also observed in Fig. 10b for the case of the day with ambient temperature < 10 ºC, where the PV-T DC power is even lower. If the active cooling system were working as expected, the PV-T module should have been at lower temperature, so there might be a problem with the manufacturing of the commercial PV-T module, without an appropriate thermal contact between the back of the PV module and the cooling circuit, as the results show. According to the graphs, the PV modules in the PV-T systems are working under the same conditions than the purely PV systems, i.e., as if they did not have an active cooling circuit on the back.

To analyse the bad thermal contact problem of the PV-T system, Fig. 11 depicts the DC voltage at the Maximum Power Point (MPP) established by the microinverter and its dependence with temperature. Once again, we can observe how the PV-T system exhibits the same electrical performance as the purely PV system, for both represented days. The central part of the graph is clearly controlled by the microinverters, but no dependence with the fluid temperature from the cooling circuit is observed, supporting the hypothesis of a problem with the attachment and thermal contact between the PV and thermal parts.

Considering the microinverters performance, Fig. 12a and b show the DC and AC electrical powers for the two systems (Fig. 12a shows the PV system and Fig. 12b the PV-T system) for the clear day of maximum ambient temperature > 30 ºC, which constitutes hot weather operating conditions, not ideal for inverters in general. Despite the adverse environmental conditions, the microinverters achieved a very high efficiency, up to 96.3 %, showing the suitability of this configuration for systems destined to building integration. Fig. 12c depicts the working DC current of the four modules, where it can be observed the limit imposed by the microinverters point of work.

4. Conclusions

The PV module works better when it is cooled and additional energy can be extracted and applied to thermal loads, but this PV-T concept needs to solve several problems: how to absorb the heat from a PV module, how to manage the heat, how to keep the PV modules cool at high temperatures, how to replace a PV-T module in the middle of an array, and how to control the flow and pressure through the modules to minimize losses, and all this, at competitive cost.

A commercial PV-T system for BIPV has been tested vs. a purely PV system to study the real performance and advantages of this type of systems. The combined efficiency (photovoltaic + thermal) over the span of a full day could reach values up to 80 %, but this apparent high value needs to be analysed in detail to understand the true performance of the combined hybrid system.

From the experimental results, it can be observed that both systems, PV and PV-T, have a good electrical performance, efficiency range of 16.1 % - 19.1 % and 15.3 % - 18.2 %, respectively. But the PV-T system output does not benefit from the lower module temperatures that it should achieve from the active cooling in its back, presenting the same performance as the purely PV system. In some cases, the electrical output has been even lower, suggesting that the module temperature in the PV-T system was equal or higher than the purely PV modules. It might be due to an inappropriate or inexistent thermal attachment of the cooling circuit in the back of the modules during the manufacturing process or a new cooling circuit design would be necessary to improve these limitations.

Regarding thermal efficiency, it has been again lower than expected (50 % -70.4 %), only reaching adequate values in clear days with high ambient temperatures. But on cold clear days, the efficiencies were too low (50 %). Considering the tank temperatures, they have been always below the standards for hot water domestic systems (60 – 80 ºC). Exergy presents the same trend, with figures too low in comparison with electrical energy as is depicted in table III. However, both thermal efficiency and exergy figures are better than those who appear in the current scientific literature.

In conclusion, the commercial PV-T system has not performed as expected, showing problems with the integration of the active cooling in the back of the PV modules. Using only the combined efficiency can lead to misunderstanding as problems and/or limitations might not be detected, especially when working in comparison with purely PV systems. At this moment, and despite the potential of PV-T systems for BIPV due to space limitations, commercial PV-T systems are still far from PV and Thermal systems using separately.

Finally, regarding the microinverters configuration performance, it has been very positive, working at high efficiencies above 96 %, justifying its use in this type of applications.

Acknowledgements

The authors acknowledge funding from FEDER-INNTERCONECTA Programme, OPTIMA ENVOLVENTE Project, EXP 00064388/ITC-20131062.

M. Vivar acknowledges funding from the Spanish Ministry of Economy and Competitiveness, ‘Ramón y Cajal’ Programme, Grant number RYC-2015-17306.

5. References

[1] Van Helden WGJ, Van Zolingen RJCh, Zondag HA. PV Thermal systems: PV panels supplying Renewable electricity and heat. Prog Photovolt: Res Appl 2004;12:415-26.

[2] Tyagi VV, Kaushik SC, Tyagi SK. Advancement in solar photovoltaic/thermal (PV/T) hybrid collector technology. Renewable and Sustainable Energy Rev 2014;16:1383-98.

[3] Chow TT. A review on photovoltaic/thermal hybrid solar technology. Appl Energy 2010;87:365-79.

[4] Michael JJ, Iniyan S, Goic R. Flat plate solar photovoltaic-thermal (PV/T) systems: A reference guide. Renewable and Sustainaible Energy Rev 2015;51:62-88.

[5] Feng S, Fang T, Lei C, Guiyin F. Performance evaluations and applications of photovoltaic-thermal collectors and systems. Renewable and Sustainable Energy Rev 2014;33:467-83.

[6] Charalambous PG, Maidment GG, Kalogirou SA, Yiakoumetti K. Photovoltaic Thermal (PV/T) collectors: A review. Appl Therm Eng 2007;27:275-86.

[7] Kramer K, Helmers H. The interaction of standards and innovation: Hybrid photovoltaic-thermal collectors. Sol Energy 2013;98:434-9.

[8] EN 12975:2006, Thermal solar systems and components. Solar Collectors. Part 1: General Requirements, Part 2: Test Methods.

[9] ISO 9806:2017 Test methods for solar collectors, Part 1: thermal performance of glazes liquid heating collectors, including pressure drop, Part 2: Qualification test procedures.

[10] IEC 60904:2006, Photovoltaic devices. Part 1: Measurement of photovoltaic current-voltage characteristics.

[11] IEC 60904:2007, Photovoltaic devices. Part 2: Requirements for reference solar devices.

[12] Fischer S, Drück H. Standards and Certification Schemes for Solar Thermal Collectors, Stores and Systems. Energy Procedia 2014;57:2867-71.

[13] Colangelo G, Favale E, Miglietta P, de Risi A. Innovation in flat solar thermal collectors: A review of the last ten years experimental results. Renewable and Sustainable Energy Rev 2016;57:1141-59.

[14] Pathak MJM, Girotra K, Harrison SJ, Pearce JM. The effect of hybrid photovoltaic thermal device operating conditions on intrinsic layer thickness optimization of hydrogenated amorphous silicon solar cells. Sol Energy 2012;86:2673-7.

[15] Dupeyrat P, Menezo C, Rommel M, Henning HM. Efficient single glazed flat plate photovoltaic-thermal hybrid collector for domestic hot water system. Sol Energy 2011;85:1457-68.

[16] Hussain F, Othman MYH, Yatim B, Ruslan H, Sopian K, Anuar Z, Khairuddin S. An improved design of photovoltaic/thermal solar collector. Sol Energy 2015;122:885-91.

[17] Ibraim A, Othman MYH, Ruslan MH, Mat S, Sopian K. Recent advances in flat plate photovoltaic/thermal (PV-T) solar collectors. Renewable Sustainable Energy Rev 2011;15:352-65.

[18] Reddy SR, Ebadian MA, Cheng-Xian Lin. A review of PV-T systems: Thermal management and efficiency with single phase cooling. Inter J Heat Mass Transfer 2015;91:861-71.

[19] Aste N, del Pero C, Leonforte F, Manfren M. Performance monitoring and modeling of an uncovered photovoltaic-thermal (PVT) water collector. Sol Energy 2016;135:551-68.

[20] Aste N, del Pero C, Leonforte F. Water flat plate PV-thermal collectors: A review. Sol Energy 2014; 102:98-115.

[21] Kumar A, Baredar P, Qureshi U. Historical and recent development of photovoltaic thermal (PVT) technologies. Renewable and Sustainable Energy Rev 2015;42:1428-36.

[22] Jelle BP, Breivik C, Rokenes HD. Building integrated photovoltaic products: A state of the art review and future research opportunities. Sol Energy Mater Sol Cells 2012;100:69-96.

[23] Anderson TN, Duke M, Morrison GL, Carson JK. Performance of a building integrated photovoltaic/thermal (BIPVT) solar collector. Sol Energy 2009;83:445-55.

[24] Dupeyrat P, Ménézo C, Fortuin S. Study of the thermal and electrical performances of PVT solar hot water system. Energy Build 2014;68:751-5.

[25] Ibrahim A, Fudholi A, Sopian K, Othman MY, Ruslan MH. Efficiencies and improvement potential of building integrated photovoltaic thermal (BIPVT) system. Energy Convers Manage 2014;77:527-34.

[26] Fudholi A, Sopian K, Yazdi MH, Ruslan MH, Ibrahim A, Kazem HA. Performance analysis of photovoltaic thermal (PVT) water collectors. Energy Convers Manage 2014;78:641-51.

[27] Kalogirou SA, Tripanagnostopoulos Y. Hybrid PV/T solar systems for domestic hot water and electricity production. Energy Convers Manage 2006;47:3368-82.

[28] Dubey S, Tiwari GN. Thermal modeling of a combined system of photovoltaic thermal (PV/T) solar water heater. Sol Energy 2008;82:602-12.

[29] Bhattarai S, Oh JH, Euh SH, Kagle GK, Kim DH. Simulation and model validation of sheet and tube type photovoltaic thermal solar system and conventional solar collecting system in transient states. Sol Energy Mater Sol Cells 2012;103:184-93.

[30] Kalogirou SA, Tripanagnostopoulos Y. Industrial application of PV/T solar energy systems. Appl Therm Eng 2007;27:1259-70.

[31] Thipjak N, Pongpith T, Yuki U, Atsushi A. Field experiments of PV-thermal collectors for residential application in Bangkok. Energies 2012; 5:1229-44.

[32] Redpath DAG, Singh H, Tierney C, Dalzell P. An experimental comparison of two solar photovoltaic-thermal (PVT) energy conversion systems for production of heat and power. Energy Power 2012;2(4):46-50.

[33] Axaopoulos PJ, Fylladitakis ED. Performance and economic evaluation of a hybrid photovoltaic/thermal solar system for residential applications. Energy Build 2013;65:488-96.

[34] Jin-Hee K, Se-Hyeon P, Jun-Gu K, Jun-Tae K. Experimental performance of heating system with building-integrated PVT (BIPVT) collector. Energy Procedia 2014;48:1374-84.

[35] Aste N, Leonforte F, del Pero C. Design, modeling and performance monitoring of a photovoltaic-thermal (PVT) water collector. Sol Energy 2015;112:85-99.

[36] de Keizer C, de Jong M, Mendes T, Katiyar M, Folkerts W, Rindt C et al. Evaluating the thermal and electrical performance of several uncovered PVT collectors with a field test. Energy Procedia 2016;91:20-26.

[37] Solar Heat Worldwide. Global Market Development and Trends in 2016. Detailed Market Figures 2015. 2017 Edition. Solar Heating & Cooling Programme. International Energy Agency. 2017

[38] Trends 2015 in Photovoltaic Applications. International Energy Agency. 2015

[39] C. Good, I. Andresen, A.G. Hestnes. Solar energy for net zero energy buildings –A comparison beteeen solar thermal, PV and photovoltaic-thermal (PV/T) systems. Sol Energy 2015;122:986-96.

[40] Sher HA, Addoweesh KE. Micro-inverters. Promising solutions in solar photovoltaics. Energy Sustainable Development 2012;16(4):389-400.

[41] Famoso F, Lanzafame R, Maenza S, Scandura PF. Performance compasison between micro-inverter and string-inverter photovoltaic systems. Energy Procedia 2015;81:526-39.

[42] Mirzaei PA, Carmeliet J. Influence of the underneath cavity on buoyant-forced cooling of the integrated photovoltaic panels in building roof: a thermography study. Progr Photovolt: Res Appl 2015;23:19-29.

[43] Gan G. Effect of air gap on the performance of building-integrated photovoltaics. Energy 2009;34:913-21.

[44] Kurnik J, Jankovec M, Brecl K, Topic M. Outdoor testing of PV module temperature and performance under different mounting and operational conditions. Sol Energy Mat Sol Cells 2011;95:373–6.

[45] Maturi L, Belluardo G, Moser D, del Buono M. BiPV system performance and efficiency drops: overview on PV module temperature conditions of different module types. Energy Procedia 2014;48:1311-9.

[46] Skoplaki E, Palyvos JA. On the temperature dependence of photovoltaic module electrical performance: a review of efficiency/power correlations. Sol Energy 2009;83:614–24.

[47] Armstrong S, Hurley WG. A thermal model for photovoltaic panels under varying atmospheric conditions. Appl Therm Eng 2010;30:1488-95.

[48] Dubey S, Sarvaiya JN, Seshadri B. Temperature Dependent Photovoltaic (PV) Efficiency and its effect on PV production in the World – a review. Energy Procedia 2013;33:311-21.

[49] Schwingshackl C, Petitta M, Wagner JE, Belluardo G, Moser D, Castelli M et al. Wind effect on PV module temperature: analysis of different techniques for an accurate estimation. Energy Procedia 2013;40:77-86.

[50] IEC61724:1998, Photovoltaic system performance monitoring. Guidelines for measurement, data exchange and analysis.

[51] ISO9459-2:1995, Solar heating. Domestic water heating systems. Part 2: Outdoor test methods for systems performance characterization and yearly performance prediction of solar-only systems.

[52] Lauterbach C, Schmitt B, Vajen K. System analysis of a low-temperature solar process heat system. Sol Energy 2014;101:117-30.

[53] Porras-Prieto CJ, Mazarrón FR, de los Mozos V, García JL. Influence of required tank water temperature on the energy performance and water withdrawal potential of a solar water heating system equipped with a heat pipe evacuated tube collector. Sol Energy 2014;110:365-77.

[54] Fujisawa T, Tani T. Annual exergy evaluation on photovoltaic-thermal hybrid collector. Sol Energy Mat Sol Cells 1997;47:135-48.

[55] Bejan A, Tsatsaronis G. Moran MJ. Thermal Design and Optimization. New York, John Wiley & Sons 1996, USA.

[56] Evola G, Marletta L. Exergy and thermoeconomic optimization of a water-cooled glazed hybrid photovoltaic/thermal (PVT) collector. Sol Energy 2014;107:12–25.

[57] Pons M. On the reference state for exergy when ambient temperature fluctuates. Inter J Thermodynamics 2009;12(3):113–21.

[58] Yazdanpanahi J, Sarhadd F, Adeli MM. Experimental investigation of exergy efficiency of a solar photovoltaic thermal (PVT) water collector based on exergy losses. Sol Energy 2015;118:197-208.